## Summary
|  | Daylight Harvesting | High Efficiency Lighting (0.889W/SF) | Plug Load Control - Night Watchman | Plug Load Control Occupancy Sensors | High Efficiency Servers | Aerogel Wall Insulation | Insulate IDF/MDF Interior Walls | Window Film | Mechanical Duct Bridging
|  | EPM 1 | EPM 2 | EPM 3 | EPM 4 | EPM 5 | EPM 6 | EPM 7 | EPM 8 | EPM 9
Estimated Direct Cost for Project Baseline |  | 0 | 699588 | 0 | 0 | 0 | 56159 | 0 | 0 | 0
Estimated Direct Cost for EPMs |  | 8700 | 690084.5 | 0 | 20000 | 0 | 73039 | 9542 | 7500 | 23348.05
Incremental Cost without Mark-Ups |  | 8700 | -9503.5 | 0 | 20000 | 0 | 16880 | 9542 | 7500 | 23348.05
Local Tax on Material Only * | 8.75% | 380.625 | -415.7781 | 0 | 875 | 0 | 738.5 | 417.4625 | 328.125 | 1021.4772
Design Contingency | 8% | 696 | -760.28 | 0 | 1600 | 0 | 1350.4 | 763.36 | 600 | 1867.844
General Contractor General Conditions & Fee | 10% | 870 | -950.35 | 0 | 2000 | 0 | 1688 | 954.2 | 750 | 2334.805
Bonds & Insurances | 2% | 174 | -190.07 | 0 | 400 | 0 | 337.6 | 190.84 | 150 | 466.961
Incremental Cost with Mark-Ups |  | 10820.625 | -11819.9781 | 0 | 24875 | 0 | 20994.5 | 11867.8625 | 9328.125 | 29039.1372
* Material, as % of total cost (assumption) | 50%

## EPM 1
EPM 1
Daylight Harvesting
Costing Assumption:
Each light in daylight zone (within 20 ft of windows) were counted. Assumed 20 lights per control circuit. Added 5% to count.
Project Baseline |  |  |  |  | Energy Performance Measure
No daylight sensors. |  |  |  |  | Install daylight sensors/photocells in the perimeter spaces to reduce lighting requirements when there is sufficient natural light. Independent controls for each luminary.
Description | Quantity | Unit | Rate | Total | Description | Quantity | Unit | Rate | Total
No photo sensors | 0 | ea | 0 | 0 | LuxSense Ambient light sensors | 29 | ea | 100 | 2900
|  |  |  | 0 | Wiring & Install | 29 | ea | 200 | 5800
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0

## EPM 2
EPM 2
High Efficiency Lighting (0.889W/SF)
Costing Assumption:
Prices shown are per floor. Assumes 20 fixtures per occupancy sensor. Price includes installation, materials, conduits and circuits.
Project Baseline |  |  |  |  | Energy Performance Measure
Current lighting energy use 1.3 W/SF |  |  |  |  | Install high efficiency lighting with occupancy sensors with a lighting density of 0.889 W/SF
Description | Quantity | Unit | Rate | Total | Description | Quantity | Unit | Rate | Total
KA -38W, T8 @0.77 BF | 186 | ea | 794 | 147684 | KA - T5 28W lamp @0.75 BF | 190 | ea | 708 | 134520
KA/d - 28W/T5 @0.85BF | 72 | ea | 837 | 60264 | KA/d - T5 26W @ 0.85BF | 78 | ea | 837 | 65286
KB - 14W/LED downlight | 35 | ea | 1093 | 38255 | KB - 10W BevelLED 4.5" Sq. | 35 | ea | 1180 | 41300
KB/d - 14W/LED downlight with dimmer | 12 | ea | 1180 | 14160 | KB/d 10W BevelLED 4.5" Sq. with Dimming Ballast | 12 | ea | 1287 | 15444
KB-2 14W/LED downlight | 5 | ea | 1093 | 5465 | KB-2 10W BevelLED 4.5" Sq. | 5 | ea | 1180 | 5900
KC - 14W/LED downlight recess mounted adjustable | 31 | ea | 1136 | 35216 | KC-10W BevelLED 4.5" Sq. | 31 | ea | 1180 | 36580
KC/d - 14W LED downlight dimmable | 21 | ea | 1180 | 24780 | KC/d -10W BevelLED 4.5" Sq. with Dimming Ballast | 17 | ea | 1287 | 21879
KE - 10W LED MR16 downlight dimmable | 34 | ea | 1093 | 37162 | KE - 10W LED MR16 | 36 | ea | 1093 | 39348
KF - 3W/LF Blue LED Strip | 430 | LF | 257 | 110510 | KF - 3W/LF Blue LED Strip | 360 | LF | 257 | 92520
KG - T5 29W @0.88BF dimming balast | 64 | LF | 236 | 15104 | KG - 25W T8 lamp @ 0.85BF | 64 | LF | 279 | 17856
KG-1 - T5 29W @0.88BF recess mounted | 98 | LF | 236 | 23128 | KG-1 - 25W T8 lamp @ 0.85BF | 85 | LF | 279 | 23715
KL - recessed 2 lamp T5, 29W @ 0.85BF | 22 | ea | 750 | 16500 | KL -Recessed Mounted 2 lamp 2' x2' with Electronic Ballast @ 0.75 | 24 | ea | 729 | 17496
KM - scope says not used | 1 | ea | 558 | 558 | KM - 2 lamp ballast at 0.75 BF | 1 | ea | 558 | 558
KN - Custom RGB LED panels 11W/LF | 60 | LF | 343 | 20580 | KN - Custom RGB LED panels 11W/LF | 60 | LF | 343 | 20580
KR - LED linear under cabinet task light | 12 | LF | 536 | 6432 | KR - LED linear under cabinet task light | 12 | LF | 536 | 6432
KS - Ceiling recessed flourescent slot | 37 | LF | 215 | 7955 | KS - Low wattage LED strip | 18 | LF | 322 | 5796
KT/C - Ceiling recessed flourescent (2 lamp) with energy saving ballast | 57 | LF | 279 | 15903 | KT-C -Low wattage LED strip | 56.5 | LF | 365 | 20622.5
KT/W - Wall recessed flourescent with energy saving ballast | 40 | LF | 300 | 12000 | KT/W - Low wattage LED strip | 40 | LF | 408 | 16320
KU - Custom LED Occupancy Indicator | 8 | ea | 1287 | 10296 | KU - Custom LED Occupancy Indicator | 8 | ea | 1287 | 10296
KV - T8 with dimming, 100W, @0.71 ballast factor | 14 | ea | 2574 | 36036 | KV -4' x 4' 2 lamp lutron ballast @ 0.7 BF | 14 | ea | 2574 | 36036
Ceiling Occupancy Sensors, F/I | 77 | ea | 800 | 61600 | Ceiling Occupancy Sensors, F/I | 77 | ea | 800 | 61600

## EPM 3
EPM 3
Plug Load Control - Night Watchman
Costing Assumption:
**No estimate can be made at this time. Night watchman may be contacted to set up an assesment of client needs and provide prices. **Bloomberg already has a license for other software from this company.
Project Baseline |  |  |  |  | Energy Performance Measure
No computer energy management in place beyond employee voluntary shutdown. |  |  |  |  | Install Night Watchman software to back up and shut down computers during unoccupied periods.
Description | Quantity | Unit | Rate | Total | Description | Quantity | Unit | Rate | Total
No additional software | 0 | ea | 0 | 0 | Night watchman software | 0 | ea |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0

## EPM 4
EPM 4
Plug Load Control Occupancy Sensors
Costing Assumption:
Each workstation received one power bar with active control. Price is per floor and assumes 200 workstations
Project Baseline |  |  |  |  | Energy Performance Measure
No plug load control |  |  |  |  | Provide outlets with active control that turn off power completely when the space is unoccupied.
Description | Quantity | Unit | Rate | Total | Description | Quantity | Unit | Rate | Total
No change to design | 0 | ea | 0 | 0 | Power bar with active plug load kill switch | 200 | ea | 100 | 20000
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0

## EPM 5
EPM 5
High Efficiency Servers
Costing Assumption:
Although we are not able to price this option without more information, changing servers and/or virtualization has no direct impact on construction cost and is a software decision. It will be important to consider the change in cooling requirements that result when new equipment is introduced. This may require additional cooling/electrical capacity.
Project Baseline |  |  |  |  | Energy Performance Measure
IT Loads have been estimated in the IDF/MDF rooms as 50W/SF. No information is provided about server make/model or cooling strategy. |  |  |  |  | To reduce energy consumption by 50% as described in the EPM a better understading of current equipment and virtualization startegy is necessary. Equipment updating may be required before virtualization is possible.
Description | Quantity | Unit | Rate | Total | Description | Quantity | Unit | Rate | Total
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0

## EPM 6
EPM 6
Aerogel Wall Insulation
Costing Assumption:
Applies on floors 16-21 (each floor insulation area 4220 SF). Price provided is for a single floor. Please see second option on detail sheet.
Project Baseline |  |  |  |  | Energy Performance Measure
No information provided about exisiting insulation. No additional cost associated with maintaining this insulation. |  |  |  |  | Add insulation (aerogel 'Spaceloft') to the inside of perimeter walls.
Description | Quantity | Unit | Rate | Total | Description | Quantity | Unit | Rate | Total
Demo | 4220 | SF | 2 | 8440 | Demo | 4220 | SF | 2 | 8440
New GB partitions | 4220 | SF | 10 | 42200 | New GB partitions with aerogel insulation | 4220 | SF | 14 | 59080
Paint | 4220 | SF | 1 | 4220 | Paint | 4220 | SF | 1 | 4220
Wall base | 433 | LF | 3 | 1299 | Wall base | 433 | LF | 3 | 1299

## EPM 7
EPM 7
Insulate IDF/MDF Interior Walls
Costing Assumption:
Assumes only portion in tenant space. Please see second option in Details.
Project Baseline |  |  |  |  | Energy Performance Measure
Assume standard interior insulation around IDF/MDF rooms. R-2.5 |  |  |  |  | Add insulation to interior walls around IDF/MDF rooms on floors 16-21 to increase to R-12.5
Description | Quantity | Unit | Rate | Total | Description | Quantity | Unit | Rate | Total
Walls are complete with standard insulation |  |  |  |  | Demo | 605 | SF | 2 | 1210
[5 empty] | New GB partitions with R-12.5 insulation | 605 | SF | 12 | 7260
[5 empty] | Paint | 605 | SF | 1 | 605
[5 empty] | Wall base | 39 | LF | 3 | 117
[5 empty] | Remove, Store & Reinstall Door | 1 | ea | 350 | 350

## EPM 8
EPM 8
Window Film
Costing Assumption:
Applies to floors 16-21 only. Windows are 8' high. Price shown is per floor.
Project Baseline |  |  |  |  | Energy Performance Measure
No film on windows. U value of 0.6, Solar heat gain coefficient of 0.7. |  |  |  |  | Apply film to existing glazing to control solar heat gain. Solar heat gain coefficient reduced to 0.5.
Description | Quantity | Unit | Rate | Total | Description | Quantity | Unit | Rate | Total
No change from baseline | 0 | ea | 0 | 0 | Installed cost window film | 2500 | SF/Floor | 3 | 7500
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0

## EPM 9
EPM 9
Mechanical Duct Bridging
Costing Assumption:
MP supply duct pressure class 3. The static pressure sensor is assumed in the base design, so a new one is not needed for duct bridging.
Project Baseline |  |  |  |  | Energy Performance Measure
As designed per M-111.00 dated 06/01/12 |  |  |  |  | Bridge the duct betweent the two medium pressure supply lines. Supply redundancy helps with air flow and single AHU down time.
Description | Quantity | Unit | Rate | Total | Description | Quantity | Unit | Rate | Total
|  |  |  | 0 | New Sheet Metal | 720 | lbs | 10 | 7200
|  |  |  | 0 | 1" Ridig Insulation w/ VB | 455 | sf | 15.71 | 7148.05
|  |  |  | 0 | Auto Louver Damper 66x14 | 2 | ea | 2887.5 | 5775
|  |  |  | 0 | Auto Louver Damper 60x14 | 1 | ea | 2625 | 2625
|  |  |  | 0 | Wiring | 3 | ea | 200 | 600
|  |  |  | 0 |  |  |  |  | 0
|  |  |  | 0 |  |  |  |  | 0